## Slide 1: RIG and other things
VMware
  System dynamically packs the load to use only the smallest number of hypervisors needed and puts the others in standby
R89 Datacentre
  Discussions ongoing about raising the chilled water temperature 0.5o or 1.0o C and what savings and PUE reduction that might provide. 1% reduction in PUE is ~ 120000 kWh/yr or ~£30k /yr
  R89 PUE yearly average is ~1.3, currently peaking at 1.45
  Most PDUs provide power monitoring at the bank level not per socket
Disposals via GreenMachine

## Slide 2: UPD room
New data hall in R89 has a maximum capacity of ~600kW
Newer more efficient chillers
All racks with rear door coolers
Aiming at PUE of 1.2.
All PDU strips have individual power socket metering so we will be able to monitor individual servers