## Slide 1: Operation & upgrades on the T2K hadron absorber towards 1.3 MW operation
T. Nakadaira
High Energy Accelerator Research Organization (KEK) IPNS / J-PARC
for
J-PARC neutrino facility

## Slide 2: Contents
Overview of beam dump @ J-PARC neutrino beam-line
Operation experience
Upgrade for 1.3MW operation

## Slide 3: Overview
Facility equipment for 2ndary BL is installed in TS and two utility buildings.
Decay Volume
Beam dump
Secondary beam line
↑
“NU3”
Neutrino Utility Building #3
Neutrino Utility Building #2
“NU2”
↓
Target Station

## Slide 4: DV & BD
Beam dump
Decay Volume
Beam dump
Secondary beam line
Target Station

## Slide 5: Hadron absorber: Segmented graphite w/ Al cooling block
Gap ΔＹ 0.2mm
Assuming heat transfer coefficient between the graphite block and the cooling module = 4.5kW/m2K
~ 500 deg.
DV and Beam damp designed for 3MW beam power.
beam axis
2 (H)× 7 (V)
= 14 modules

## Slide 6: BD: Temperature monitoring
Screen shot during ~490kW beam operation.

## Slide 7: DV: Temperature monitoring
Screen shot during ~490kW beam operation.

## Slide 8: CW system
Target Station
Decay Volume
Beam dump
Secondary beam line
Cooling system in TS & NU2
for upstream part
Cooling system in NU3
for downstream part
Separated 2 systems

## Slide 9
Upgrade water cooling system ( 750kW  1MW )
The circulation pumps and the heat exchangers will be replaced to more large capacity ones
Chillers and cooling towers will be added.
Procurement of equipment is on going.  Installation in ~2025.

## Slide 10: DV&BD is working well in 510kW operation.
Decay Volume
Target Station
Beam Dump
Vessel filled w 1atm. He gas
L=~110m,V=1,600m3
OA2o
OA2.5o
Beam Transport
From RCS to MLF
6m-thick concrete wall
OA3o
Muon pit
No water leak happened inside He vessel (except for horns).
Water leak can be detected at drain ports at TS-B2 machine room and muon pit.
Inspection after the big earthquake in 2011.

## Slide 11: Redundant CW channels for 1.3MW
If water leak happen, we can run without troubled water loop by closing the valves .

## Slide 12: Issues for CW system for DV & BD.
Due to the beam operation, the pre-filters for degasfiers are clogged by “black material”.  It is necessary to adjust CW system regulally.
We have tried several filter configuration (mesh size: 0.5μm/1.0μm/10μm and their combination) but issue not solved yet. We have to open bypass of filters.  The membrane degasfier has been radio-activated
Black material is also adhere to strainer, pump, etc.  Additional (radiation) work for maintenance.
Pre-filter + Degasifier
Strainer coated
by black color
CW pump maintenance

## Slide 13: CW “Black” issues
It is necessary to adjust flow-rate for pre-filters/by-pass periodically during the beam operation period.  It is necessary to stop beam for >8hours because it is installed in access controlled area. - Remote adjustment system is implemented for TS and is under preparation for NU3.
We should replace filters by new one every year.  Piles of garbage become higher and higher.
We plan to try “magnetic strainer” to solve this issue.
Serial Pleats filters(0.5um)
Bag-type
filter/strainer (5um)
B2F
Pump
Every rooms in NU3 are occupied by used pre-filters.

## Slide 14: Summary
Decay Volume and Hadron absorber (Beam dump) of J-PARC neutrino beam-line is designed for 3MW.  Cooling capability has redundancy for 1.3MW operation.
Cooling water system for secondary beam-line will be reinforced for 1.3MW. Procurement of equipment is on going and will be installed in ~2025.
So far, DV and beam dump systems are working well without water leak in the He vessel.
Unexpected issue: “Black material” in CW is still under investigation.
  Countermeasures to deal with work under high radiation environment is considered.
  Accumulating activated waste is a real pain in the neck. To be solved.

## Slide 15
Ion Exchanger
(Not used: it will erode
Carbon steel)
Pre-filter + Degasifier
Irradiation
By Be7(53d) + Mn54(1yr)
3~4mSv/h on contact
Decrease of flow rate
  Hollow fiber membrane
Strainer coated by black color
** Flowrate recovers when beam is off
Black layer problem in carbon steel water cooling pipes
Clogging by colloidal Be7 (+ black skin) by 1~2month
Open Bypass