## Slide 1
Installation Project Status
Extreme Photonics Applications Centre (EPAC)
Steph Tomlinson EPAC Senior Engineer Manager
Jodie Smith EPAC Installation Manager

## Slide 2
Outline of Content
Progress Since Building Handover
  Surveys
  LN2 tank and pipework
  Lab specific services
  Fire proofing
  Pump laser installation
  EA1 Preparation Works
Forward Look
Challenging Installation Activities
  Beam propagation
  Compressor chamber install

## Slide 3
Stability - Building Vibration Survey
Stability
  Complex beam transport across the whole facility
  Design structures and mounting systems to avoid resonances
  Aim for high stiffness structure with natural frequency greater than 100Hz
Vibration Data
  Baseline survey through entire building prior to any installation
  5GB of data collected on all critical floors and walls
  Impact of ISIS Facility

## Slide 4
Stability - Building Vibration Survey
NIF floor spec
50Hz peak occurs when ISIS is operating, but PSD is an order of magnitude less than seen in Gemini
10-9
10-9
10-10
10-10
Low levels of vibration above 60Hz
Peaks at 30Hz, 50Hz, 190Hz

## Slide 5
Alignment Nest and Survey
Building Network Survey Reference (175 in total)
Component Survey Reference
Laser Survey Equipment
Network set-up across building
Complete survey of walls and floors
Installation in any area to same datum
Now in use for component installation

## Slide 6
Installation of the LN2 tank
400l tank to store LN2
Required to supply the cryostats for the pump laser system
Estimate the need to fill every two weeks during operation

## Slide 7
Installation of the LN2 pipework for pump laser
LN2 pipework to transport LN2 from outside tank into the pump room for use in cryostats
Normal Exhaust lines to take cold GN2 (boil off) to safe external location
Emergency Exhaust (from pressure relief valves) lines to take any gases to safe external termination point

## Slide 8
Installation of cable containment pump laser and rack room
Last ISTAC this proposed services layout was shown for the pump laser area
The 3 tiered cable gantry and interlock trunking has been installed throughout this area.
  Top layer power
  Mid layer control and data cables
  Bottom layer mechanical services (gas and water)

## Slide 9
Pump laser equipment install
Optical tables installed into the room
  Including pre-built front end table
Amplifier heads and cryostats installed
  Including base plate fixed to the floor to allow easy repositioning
Notes: Using alignment survey nests essential for ensuring equipment in the correct place. – issue with the floor level

## Slide 10
Challenging Installation: Fire proofing
Fire proofing multi-layer gantry
Modification of fire doors for interlocks
Fire compartments on the 2nd floor are breached as a result of the apertures between rooms for services and lasers
Fire stopping deployed must allow for future installation of services
Fire doors fixtures are subject to particular regulations

## Slide 11
Ground Floor look ahead 2022 - 2024
Jan '23
Apr '23
Jul '23
Oct '23
Jan '24
Apr '24
Jul '24
Oct '24
Floor Preparation Nov 22 - Jan 23
Focusing Chamber Jul – Sep 23
Beam Propagation Pit Sept – Nov 23
Beam Propagation Dec 23 – Mar 24
EA1 Main Services Jan – Dec 23
EA1 Specific Services Feb – Mar 24
Beam Prop ready Tue 27/08/24
EA1 complete Tue 17/12/24
Target Chamber Sep 23 – Jan 24
Focussing Chamber and Translating Base |  | 
Activity | Start | End
Floor Preparation | Nov 22 | Jan 23
Installation | Jul 23 | Sep 23
Beam Propagation Pit & Diagnostics |  | 
Activity | Start | End
Installation | Sep 23 | Nov 23
Target Chamber and Internals |  | 
Activity | Start | End
Installation | Sep 23 | Jan 24
Beam Propagation |  | 
Activity | Start | End
Installation | Dec 23 | Mar 24

## Slide 12
Second floor look ahead 2022 to 2023
Floor plan with key dates shown
Pump Laser |  | 
Activity | Start | End
Services | Aug 22 | Dec 22
Installation | Nov 22 | Jun 23
Front End |  | 
Activity | Start | End
Services | Jan 23 | Mar 23
Installation | Mar 23 | Oct 23
Compressor & Switchyard Area |  | 
Activity | Start | End
Preparation Work | Jan 23 | Mar 23
Beam Propagation |  | 
Activity | Start | End
Preparation Work | Jan 23 | Mar 23
Installation | Jun 23 | Sept 23
Sep '22
Nov '22
Jan '23
Mar '23
May '23
Jul '23
Sep '23
Nov '23
Pump Laser Services Aug – Dec 22
Front End Services Jan – Apr 23
Ti-Sapphire Services Apr – Aug 23
Pump Laser Installation Nov 22 – Jun 23
Front End Installation Mar – Oct 23
Compressor & Beam Prop Prep Jan – Mar 23
Beam Propagation Installation Jun – Sept 23
Ti-Sapphire Installation May – Aug 23
Front End ready Fri 27/10/23
Pump ready Thu 28/09/23

## Slide 13
Switchyard |  | 
Activity | Start | End
Services | Oct 23 | Sept 24
Installation | Jan 24 | Jun 24
Compressor |  | 
Activity | Start | End
Preparation Work | Jan 23 | Mar 23
Chambers Install | Nov 23 | Jan 24
Internals Install | Jan 24 | Apr 24
Ti-Sapphire |  | 
Activity | Start | End
Services | Mar 23 | July 23
Installation | May 23 | Nov 23
Sep '23
Nov '23
Jan '24
Mar '24
May '24
Jul '24
Sep '24
Nov '24
Compressor Installation Nov 23 – Jan 24
Ti-Sapphire Installation B Sept – Nov 23
Switchyard and Compressor Input Installation Feb – Jun 24
Riser Services Sept – Nov 23
Switch & Comp Services Jun – Sept 24
Front End ready Fri 27/10/23
Pump ready Thu 28/09/23
Ti-Sapphire ready Tue 04/06/24
Beam Prop ready Tue 27/08/24
Second floor look ahead 2023 to 2024

## Slide 14
Challenging Installations
Majority of installation activities within normal CLF scope through facility upgrades and projects such as HILASE and D100X:
  Optical tables & support structures,
  Mounts and optics,
  Large vacuum chambers and vacuum systems
  Mechanical and electrical services
  Cryostats and cooling systems
Challenging installations are where:
  Large crane operations and very complex lifting activity
  Restricted access or limited local lifting provision
  Civil engineering or building activities required

## Slide 15
Challenging Installation: Beam Propagation
Priority installation activity as requires space for a crane at top of the riser
Challenging due to:
  Assembly spanning three floors
  Assembly passing through bunker wall
  Restricted height at second floor
  Restricted access in some areas
  Maintaining cleanliness for vacuum use
  Delicate sealing surfaces

## Slide 16
Challenging Installation: Beam Propagation
Install activities
  Chemical anchors support brackets
  Lifting
  Alignment with survey network
  Sealing and leak checking of each section
  Fire Proofing
Requires a combination of:
  External expertise
  CLF expertise
Ground Floor
First Floor
Pit Floor
Second Floor

## Slide 17
Challenging Installation: Compressor Chamber
Install activities
  Preparation of floor & cast base plates
  Removal of demountable wall and building cladding
  Delivery to site
  Lift onto roof and through aperture
  Position, Survey and Affix to base supports
  Site acceptance Test (Leak Check)
  Installation of internal components

## Slide 18
Challenging Installation: Compressor Chamber
Aperture in cladding
External Crane loading area
Challenging due to:
  No overhead lifting provision in laboratory
  Access through an aperture in weather sealed wall
  External crane loading area floor loading
  Restricted height in laboratory
  Inclement weather in November
Structural Engineering Assessments
Planning to engage lifting company

## Slide 19
Installation Summary
Survey network established and in use
Baseline vibration dataset obtained allowing changes to be monitored
Experienced staff with required skill sets for majority of installation activities
External expertise being obtained for challenging installations

## Slide 20
@STFC_Matters
Science and Technology Facilities Council
Science and Technology Facilities Council
Thank you
Extreme Photonics Applications Centre (EPAC)
Notes: The abstract pattern can be removed or repositioned if required. Be careful to ‘Send to Back’ so that it does not obscure any important information.

## Slide 21
Second floor look ahead 2022 - 2023
Floor plan with key dates shown
Start Mon 08/08/22
Sep '22
Nov '22
Jan '23
Mar '23
May '23
Jul '23
Sep '23
Nov '23
Pump Laser Services Mon 15/08/22 - Fri 23/12/22
Front End Services Mon 09/01/23 - Mon 03/04/23
Ti-Sapphire Services Tue 04/04/23 - Mon 07/08/23
Pump Laser Installation Mon 07/11/22 - Fri 16/06/23
Front End Installation Fri 31/03/23 - Fri 27/10/23
Compressor & Beam Prop Prep Mon 16/01/23 - Fri 31/03/23
Beam Propogation Installation Fri 30/06/23 - Fri 22/09/23
Ti-Sapphire Installation A Fri 05/05/23 - Thu 03/08/23
Front End ready Fri 27/10/23
Pump ready Thu 28/09/23

## Slide 22
Second floor look ahead 2023 - 2024
Sep '23
Nov '23
Jan '24
Mar '24
May '24
Jul '24
Sep '24
Nov '24
Compressor Installation Fri 24/11/23 - Wed 31/01/24
Ti-Sapphire Installation B Mon 25/09/23 - Fri 17/11/23
Switchyard and Compressor Input Installation Thu 01/02/24 - Wed 19/06/24
Riser Services Mon 25/09/23 - Fri 17/11/23
Switch & Comp Services Thu 20/06/24 - Wed 11/09/24
Front End ready Fri 27/10/23
Pump ready Thu 28/09/23
Ti-Sapphire ready Tue 04/06/24
Beam Prop ready Tue 27/08/24
EA1 complete Tue 17/12/24

## Slide 23
Ground Floor look ahead 2022 - 2024
Jan '23
Apr '23
Jul '23
Oct '23
Jan '24
Apr '24
Jul '24
Oct '24
Floor Preparation Mon 21/11/22 - Fri 20/01/23
Focussing Chamber Fri 07/07/23 - Thu 31/08/23
Target Chamber Fri 10/11/23 - Thu 01/02/24
Beam Propagation Pit Fri 01/09/23 - Thu 26/10/23
Beam Propagation Fri 02/02/24 - Thu 28/03/24
EA1 Main Services Mon 23/01/23 - Fri 22/12/23
EA1 Specific Services Fri 02/02/24 - Thu 28/03/24
Beam Prop ready Tue 27/08/24
EA1 complete Tue 17/12/24